Construction Safety and Health
Outreach Program

U.S. Department of Labor
OSHA Office of Training and Education
May 1996

Common Fire Extinguishing Agents

WATER

- Removes heat

- Effective on Class A fires

- Inexpensive

- Plentiful

- Non-toxic

Disadvantages:

- Conducts electricity

- May spread Class B fires

- Freezes in cold climates

- May carry pollutants as run-off water

CARBON DIOXIDE (CO2)

- Reduces oxygen to less than 15%

- Effective on Class B and C fires

- No residue

- Relatively inert

Disadvantages:

- Generally >35% concentration by volume required for total flooding system

- Toxic to humans at >4% by volume

- Not the best agent for smoldering deep-seated fires (maintain concentration for >20 minutes)

- Dissipates rapidly - allows reflash

- Has a cooling/chilling effect on some electronic components

- Vapor density = 1.5 (collects in pits and low areas)

DRY CHEMICAL

- Interrupts chemical reactions

- Sodium bicarbonate (baking soda)

- Very effective on Class B and C fires

- Not considered toxic

Disadvantages:

- Leaves a residue

- Obscures vision

- Not good on deep-seated Class A fires

- Absorbs moisture and may "cake" within container

- May be irritating

- Nozzle pressure may cause burning liquids to splash

MULTIPURPOSE DRY CHEMICAL

- Interrupts chemical reactions

- Ammonium phosphate

- Effective on Class A, B, and C fires

- Non-conductive

Disadvantages:

- Obscures vision

- More irritating than ordinary dry chemical

- Nozzle pressure may cause burning liquids to splash

HALON TERMINOLOGY

Halon 104: Carbon tetrachloride (CCl4) Halon 1211: Bromochlorodifluoromethane (CBrClF2) Halon 1301:

Bromotrifluoromethane (CBrF3)

C

F

Cl

Br

1

0

4

-

1

2

1

1

1

3

0

1

HALON 1301

- Interrupts chemical reactions

- Bromotrifluoromethane

- Effective on Class A, B, and C fires

- Not acutely toxic at <10% by volume

- Generally used at <7% by volume

- No residue

- No chilling effect on electronic parts and components

Disadvantages:

- Acutely toxic at >10% by volume (anesthetic and cardiac effects)

- Delayed effects and effects of chronic exposure not well known

- Toxic decomposition products are generated by fire

- Vapor density = 5 (collects in pits and low areas)

- Production restricted per Montreal Protocol due to depletion of ozone layer

HALON 1301

DECOMPOSITION PRODUCTS

- Hydrogen fluoride (HF)

- Hydrogen fluoride (HF)

- Hydrogen bromide (HBr)

- Bromine (Br2)

- Carbonyl Fluoride (COF2)

- Carbonyl Bromide (COBr2)

HALON 1211

- Interrupts chemical reactions

- Bromochlorodifluoromethane

- Effective on Class A, B, and C fires

- No residue

- May be sprayed (Boiling Point = 25oF)

- Used in portable fire extinguishers

Disadvantages:

- Acutely toxic at >4% by volume (dizziness, impaired coordination and cardiac effects)

- Must be used at >5% by volume

- Toxic decomposition products are generated by fire

- Vapor density = 5.7 (collects in pits and low areas)

- Production restricted per Montreal Protocol due to depletion of ozone layer

HALON 1211

DECOMPOSITION PRODUCTS

- Hydrogen bromide (HBr)

- Hydrogen chloride (HCl)

- Hydrogen fluoride (HF)

- Bromine (Br2)

- Chlorine (Cl2)

- Fluorine (F2)

- Carbonyl bromide (COBr2)

- Carbonyl chloride (COCl2)

- Carbonyl fluoride (COF2)